Seneca Gaming Corporation

Generator Maintenance Services

RFP #SGC-0073-25SDH

November 25, 2025

Confidential

Table of Contents

I.	Introduction	3

II.	RFP Objective	3

III.	Scope of Services	3

A.	Equipment	3

B.	Services	3

C.	Schedules	5

D.	Replacement Parts	5

E.	Identified Repairs	5

F.	Contractor Personnel	5

G.	Working Hours	5

H.	Maintenance Schedule	5

I.	Service Reports	5

IV.	RFP Administrative Information	6

A.	Contact Information	6

B.	Schedule of Events	6

C.	Intent to Bid	6

D.	Bidder Questions	6

E.	Submission of Proposals	6

F.	Proposal Format	6

G.	Conditions	8

H.	Proposal Evaluation/Vendor Selection	8

I.	General Bidder Information	9

J.	SGC Standard Terms and Conditions	9

V.	Provisions Applicable to the Contract	10

A.	Agreement Term	10

B.	Pricing and Payment Terms	10

C.	Tax Exempt Status	10

D.	Payment Terms	10

VI.	Supplemental Bidder Information	10

A.	Business Continuity	10

B.	Conformity of Proposal with SGC Requirements	10

VII.	Vendor Requirements	10

A.	Proposal	10

B.	Standard Service Agreement	10

C.	Seneca Nation Business Registration Fee (SNIBRF)	11

VIII.	Bidder Certifications and Representations	12

# Introduction

Seneca Gaming Corporation is a wholly owned, tribally chartered corporation of the Seneca Nation of Indians (the “Nation”) which operates all of the Nation’s Class III gaming operations in Western New York.

Seneca Gaming Corporation, through its wholly owned subsidiaries, owns and operates Seneca Niagara Resort & Casino in Niagara Falls, New York, Seneca Allegany Resort & Casino in Salamanca, New York, and Seneca Buffalo Creek Casino in Buffalo, New York.

For additional information, please visit our website at www.Senecacasinos.com.

# RFP Objective

Seneca Gaming Corporation (hereinafter referred to as SGC) is seeking a qualified Generator Service contractor to provide necessary labor and parts to perform routine scheduled preventive maintenance services to facility back-up generators and fire pumps at all three properties on a scheduled basis and/or as requested by the owner to maintain the units in an operable condition in accordance with the specific tasks noted below and the Original Equipment Manufacturer (O.E.M.) recommendations.

# Scope of Services

The facility back-up generators are as follows:

## Equipment

## Services

The specific preventive maintenance services shall include at a minimum the following tasks for the engine and generator systems.  This list is not intended to be all inclusive for each and every facility back-up generator.  The contractor shall also comply with the specific recommendations of the O.E.M. for the preventive maintenance and for all parts/materials/fluid requirements.

All service visits:

- Complete overall generator inspection for visual damage, cleanliness, wear, or overheating, inclusive of all fuel tanks, fuel lines, connections, vents, fluid leaks, air leaks, ventilation systems, bus bar connections, ATS, etc.

- Check all frame grounding points to ensure grounding wires are secure to the ground rods.

- Clean engine compartment as needed.

- Perform an engine test run for a minimum of 15 minutes to allow the engine oil to heat up to normal operating temperatures and check for proper alternator voltage. Record oil pressure, fuel pressure, charging amps, voltage and frequency.

- Inspect the enclosure, as well as all mechanically or motor operated louvers to assure free movement and proper operation.

- Verify operation of enclosure electric unit heater.

Level 1 service:

- Run the generator (typically no‐load, automatic transfer switch exercise cycle).

- Verify that the unit ran and has no alarms or warnings.

- Check and record engine fuel levels.

- Ensure that the generator is in “Auto” mode, for automatic startup.

- Check that the circuit breaker is closed. Exercise circuit breaker open and back closed a minimum of 3 times. Assure that breaker is left in closed position. Verify with facility personnel that a “MCB open” alarm was initiated via Building management system, each time breaker is opened.

- Make sure there are no ﬂuid leaks.

- Check engine coolant level.

- Check engine oil level.

- Check the battery charger. Record current and voltage of charging circuit.

- Run the generator (with load, automatic transfer switch exercise cycle) - not always performed due to the sensitivity of the slot machines on the gaming floor.

- Check and record the battery electrolyte level and speciﬁc gravity.

- Check battery cables and connections. Clean, tighten, and apply corrosion inhibitor sealant.

- Drain condensation traps.

- Inspect drive belts.

- Inspect the coolant heater.

- Check coolant lines, hoses, and connections.

- Check for oil leaks and inspect lubrication system hoses and connectors.

- Check for fuel leaks and inspect fuel system hoses and connectors.

- Inspect the exhaust system, muﬄer and exhaust pipe.

- Check and clean air cleaner units.

- Inspect air induction piping and connections.

- Inspect the DC electrical system, control panel and accessories.

- Inspect the AC wiring and accessories.

- Check and test alarm sending units, pre-alarms, and safety shutdowns.

- Check remote annunciator operation.

- Obtain engine oil and coolant samples. Send to qualified laboratory for analysis and report.

Level 2 service:

- Perform all services listed in level 1 service above.

- Change engine lubricating oil and ﬁlters, including primary lubrication and bypass filters.

- Change the fuel ﬁlter.

- Change the air ﬁlters if necessary. (If not needed, leave new filters for owner’s inventory)

- Clean the crankcase breather.

- Flush the cooling system (as needed based upon previous visit coolant analysis) Price coolant flush as separate line item in quote.

- Fuel testing and reconditioning (reconditioning shall be priced separately, and performed if needed after fuel testing).

- Remove water from fuel tank (as needed based upon fuel testing).

- Inspect engine cooling fan and fan drives for excessive wear or shaft wobble.

- Check all pulleys, belt tensioners, slack adjusters & idler pulleys for travel, wear, and overall condition.

## Schedules

    - Niagara Falls property–

      - Detailed in Exhibit A tab- “NF Schedule”

    - Buffalo Creek and Allegany Properties-

      - Preventative Maintenance (Level II) May 2026, 2027, 2028

      - Inspections (Level I) November 2026, 2027, 2028

## Replacement Parts

Contractor shall supply and maintain an adequate inventory of all necessary tools, equipment and normal parts/materials for the preventive maintenance tasks under this contract.

## Identified Repairs

Any repairs required beyond the standard preventive maintenance task(s) identified during the inspection, shall be documented and presented to the owner’s representative for approval prior to the commencement of any repair services.  Repairs shall only proceed upon issue of a purchase order.

## Contractor Personnel

Only factory trained, experienced and qualified back-up generator personnel shall perform the necessary generator preventive maintenance and repair work specified. All technicians shall be EPG or EGSA certified.

Contractor shall provide proper Personnel Protective Equipment (PPE) for their employees performing the work as required by OSHA and any other Federal, State, or Local codes, laws and regulations.

## Working Hours

All work shall be performed during normal working hours from 7:00am to 4:00pm weekdays.

## Maintenance Schedule

The maintenance schedule for each generator shall be consistent with that shown in Exhibit A. The contractor shall develop and maintain a maintenance log for each generator, listing all work performed, date of service and signature of technician performing the work.  A copy of this log shall be kept (in weather resistant binder or folder) in the enclosure of each generator, with an additional copy provided with each service report.

## Service Reports

Provide a detailed report to the owner’s representative after each visit for each generator.  The report shall include, at a minimum, details of the tests applied and their outcomes, preventive maintenance services that were provided including all recorded data, the parts/materials/etc. and the date, time and length of the visit. If oil or coolant analysis was required, copies of the laboratory reports shall be included. Reports shall be provided no more than 15 calendar days after the service visit.

Deficiency Reports shall be provided if critical deficiencies are identified during a service visit. Such deficiencies shall be reported immediately to facilities personnel, and electronically reported to the owner’s representative within 24hrs. An estimate to repair noted critical deficiencies shall be included with the electronic report.

# RFP Administrative Information

## Contact Information

Please use the following name and email address for all correspondence with SGC concerning this RFP.

Name 					Shelle Heaton

Telephone 				(716) 345-1594

Email					sheaton@senecacasinos.com

## Schedule of Events

RFP issue date:  			11/25/2025

Site Visit:				12/04/2025

Bid Submission Deadline: 	12/11/2025

## Intent to Bid

Potential Bidders must submit an email confirming their intent to bid to the Facilitator by the date and time indicated in the above schedule of events.

Submission of the intent to bid notice constitutes the Potential Bidder’s acceptance of the RFP schedule, procedures evaluation criteria and other administrative instructions of this RFP.

## Bidder Questions

Bidders must submit any questions to the Facilitator’s email address directly. No telephone questions will be accepted or considered.

Questions must reference the specific RFP paragraph number and page and quote the passage being questioned. SGC will respond to questions promptly and will send answers to Bidders as a group.

## Submission of Proposals

Proposals must be submitted in electronic form, preferably in Microsoft Word and/or Microsoft Excel formats.  Note: SGC’s email system rejects incoming messages with attachments exceeding 20 MB.  Bidders are encourage to confirm that the Coordinating Buyer received their bid, prior to the bid submission deadline (date and time) indicated in the above schedule of events.

The Coordinating Buyer must receive proposals on or before the bid submission deadline. Proposals received after the bid submission deadline will not be considered.

## Proposal Format

Send RFP response with all requested information answered in the format provided, 			along with any supporting attachments, electronically via email as stated in (above) 			Section E.

Bidders must complete the attached excel workbook - Exhibit A

In addition, the following documents must be sent with your RFP response:

Part-1	Bidder Representations and Certifications

A corporate officer or person who is authorized to represent Bidder must complete, sign and date the Bidder Certifications and Representations, Section VII of the RFP.

Part-2	Appendix

Appendix-A: Evidence of Insurance

Evidence of current insurance is to be provided to the satisfaction of SGC’s Risk Management Department. Insurance requirements vary depending upon the nature of the services and the degree of risk. Standard requirements include minimum $5 million general liability coverage (per occurrence and in the aggregate) [$10 million for construction-related contracts], $1 million automobile liability coverage, combined single limit, for all vehicles brought on-site, worker’s compensation and employer liability insurance in accordance with state law. Additional types of insurance, including, without limitation, professional liability insurance and network privacy/data security/cyber liability insurance, may be required in specific circumstances. SGC and related persons and entities will be additional insured under the general liability and automobile liability policies of insurance.

SGC’s Risk Management Department has discretion to increase, decrease, or dispense with insurance in appropriate cases. They may, in addition to or instead of insurance, require signature of a Waiver, Indemnification and Hold Harmless form by any individuals who will be present on SGC property.

Additional Insured language:

Seneca Gaming Corporation and their parent, Subsidiaries, Directors, Officers, Agents, representatives and Employees are named as Additional Insures on the General Liability and Automobile Liability policies. A waiver of subrogation applies on all policies, including Employer’s Liability, in favor of Seneca Gaming Corporation.

Seneca Gaming Corporation to be named as Certificate Holder:

Seneca Gaming Corporation

310 Fourth Street

Niagara Falls, NY 14303

Certificates evidencing such coverage shall be provided prior to commencement of work and renewal certificates shall be provided upon availability.

SGC’s Risk Management Department has discretion to increase, decrease, or dispense with insurance in appropriate cases. They may, in addition to or instead of insurance, require signature of a Waiver, Indemnification and Hold Harmless form by any individuals who will be present on SGC property.

For additional details, see section 22 of SGC’s Standard Terms & Conditions at https://senecacasinos.com/media/zqdd2j1f/sgc-standard-terms-and-conditions-v-10-30-20.pdf

Appendix-B:  Standard Agreements

Bidders are invited to include their standard form of agreement (preferably in Word format) to form the basis of the contract should it be awarded to them. However, SGC reserves the right to utilize its own standard form of agreement.

Part-3	Company Overview

Section 1: Company Overview

Provide a brief description of the overall organization of your company including the location of corporate headquarters, primary industries and markets served, how long the company has been in business and what experience your company has serving multi property and Native American-owned casinos and casino resorts, if any.

Section 2: References

Include a minimum of three contracts for goods or services similar to those in the RFP’s Requirement Specifications that were awarded within the last three (3) years, along with contact information for each client reference. Wherever possible, include casino and casino-resort clients in these references.

Part-4 	RFP Proposal

Section 1: Executive Summary

The purpose of this section is to summarize your proposal for SGC evaluators and decision makers. The summary should include, at minimum, key proposal elements, your vectors of competitive differentiation and an overview of your pricing model.

Section 2: Response to Requirements

Include complete responses to all requirements outlined in the Requirements Specification section of this RFP. Reponses are to follow the outline of the Requirements Specification herein (including companion documents, if any) and refer to each requirement being addressed. Requirements that cannot be supported in whole or in part should be identified as such.

Section 3: Bidder Supplemental Information

The purpose of this section is to afford Bidder an opportunity to present necessary information that was not requested.  Use this section to indicate, for example, alternative methodology or additional functionality that may be outside the scope of the RFP but could enhance the value of services delivered or potential issues that are relevant to the RFP and your proposal.

Section 4: Product and Service Delivery

This section summarizes for your standard fulfillment processes, including delivery scheduling, response to emergency orders, disaster recovery and equipment installation, maintenance, repair and replacement plans.

Part-5	Pricing Proposal and Quotes

This section summarizes Bidder’s pricing model and applicable terms. Additional offers, discounts, rebates, etc. should be noted separately.  Where applicable, pricing should cover the entire term of the contract indicated in the RFP, including any options to renew, where applicable.

## Conditions

Under no circumstances will responses be made available to other organizations, either 			wholly or in part, without Vendor’s prior written permission.

By participating in this RFP:

- Bidder agrees that you will not directly contact any SGC employee without prior written approval from SGC.  Failure to do so may revoke your invitation to participate in this RFP.

- Bidder agrees to keep confidential all information related to this RFP.  Any sharing of this information without express permission will exclude Vendor from consideration.  This RFP and all supporting attachments and related communications may not be duplicated or distributed in any form to any other company without prior written permission.

Bidder agrees that all information provided in their RFP response is valid for a 				minimum of 90 days from the response date.

All costs incurred by the bidder for participating in this evaluation will be the 				responsibility of the bidder.  SGC will not reimburse any bidder costs or expenses.

All responses to the RFP become the property of SGC.

## Proposal Evaluation/Vendor Selection

Proposals will be evaluated to determine their completeness and compliance with the mandatory requirements and qualifications specified throughout this document.  Failure to comply with one or more of these requirements may result in the proposal being rejected as non-responsive. SGC reserves the right to waive deviations it deems non-material and/or to reject any and all Proposals in its sole discretion.

The successful Bidder(s) will be notified by email of the award of contract, conditional upon appropriate licensure through SGC’s regulatory authority, the Seneca Gaming Authority (“SGA”), providing proof of insurance to the satisfaction of SGC’s Risk Management Department, and signature of a contract and/or issue of a Purchase Order. It is only following all of these actions that the successful Bidder will be considered a Vendor of SGC.

Successful Bidders must complete SGC’s Vendor Registration Form and W-9 (or equivalent for non-U.S. persons/entities). If required, they must also complete and submit to the SGA the requisite vendor license application. They are also responsible for payment of SGA processing or vendor license fees plus the Seneca Nation of Indians Business License fee as detailed in paragraph VI. I. below. Fees range from $750 to $2,500 depending upon the nature of the services. These requirements must be completed and, if applicable, the requisite SGA vendor license issued, prior to signature of the contract. Vendor licenses and fees must be renewed every two years. SGA may also, in an appropriate case, require the licensure of individual employees who perform certain services that are or may be closely associated with SGC’s casino operation. As SGA retains the discretion to make this type of determination on a case-by-case basis, SGC is unable at the RFP point in the bidding process to state definitively whether such licensure will be required in any particular case.

## General Bidder Information

This RFP does not commit SGC to award a contract, to pay any costs incurred in the preparation of the RFP, nor to procure or contract for services or supplies.

It is the policy of SGC that all Proposals are to be held unopened and confidential until after the closing date and time.  At the bid opening, Proposals will be opened by the contact Coordinating Buyer and are reviewed by a compliance representative.

Bid Validity. Bidder’s bid submission must remain valid for a minimum of ninety (90) days from the bid closing date.

Minority Bidders: SGC gives priority to Bidders who are Native American, minority, women-owned or small disadvantaged businesses. If your company falls into any of these categories or has contracted with such businesses for the purpose of the proposal, please note as such on your proposal.

Alternative Proposals (if applicable) are accepted based on the following conditions: SGC will consider alternative proposals from Bidders provided they have submitted a response based on the original requirements. The alternative Proposal will be submitted separate and apart from the basic Proposal. It is assumed that the materials included in the alternative Proposal meet all of the qualifications of the original Proposal.

Substitutes. Any recommended substitutions should be attached separately.  Products may require testing before acceptance.  Bidder’s pricing must include the conversion calculations if your size, pack, weight, etc. is not the same as the specified product(s). SGC solicits Bidders’ recommendation(s) for new products and/or services leading to lower costs.

Projected Volume. Bidders are advised that the volumes or quantities indicated on the RFP are for reference purposes only and must not be taken as guaranteed or as constituting representations by SGC. Actual volume and quantities may vary depending upon the needs of the SGC departments or business units for which the goods and/services are destined and fluctuations in the business cycle.

## SGC Standard Terms and Conditions

Any purchase order or contract flowing from this RFP (in the absence of language to the contrary in the contract) is subject to the terms and conditions hereof as well as to Seneca Gaming Corporation’s Standard Terms and Conditions which are available on the following website: https://senecacasinos.com/media/zqdd2j1f/sgc-standard-terms-and-conditions-v-10-30-20.pdf.

Reference to, or inclusion of, the Bidder’s preprinted terms and conditions with Bidder’s Proposal will not be considered as an exception to SGC Terms and Conditions.

# Provisions Applicable to the Contract

## Agreement Term

The initial term of the contract will be three years, with two options to renew in favor of SGC, each (1) year in duration (each a renewal term).

Upon expiration of the initial term and exercised renewal terms, the contract will automatically renew on a month-to-month basis, as needed to facilitate a new RFP and enter (or transition) into a subsequent new agreement.

## Pricing and Payment Terms

Please provide your most competitive pricing and any additional offers.

## Tax Exempt Status

Seneca Gaming Corporation is a governmental instrumentality of the Seneca Nation of Indians all of whose operations (except for its golf course) are on sovereign Seneca Territory.  SGC will provide a New York State tax exemption certificate issued in the name of the Seneca Nation of Indians, as applicable.

## Payment Terms

SGC standard payment terms are Net 30 days after delivery of goods and/or services and receipt of a correct invoice. Bidder is encouraged to indicate any additional early payment/ discount terms in its Proposal.  It is the policy of SGC not to provide deposits unless significant discounts or special circumstances apply.

# Supplemental Bidder Information

## Business Continuity

For RFP’s involving strategic commodities/services, provide an overview of your disaster recovery/business continuity plan (the “Plan”).  The Plan indicates how Bidder minimizes the risk of interruption to Bidder’s ability to provide the goods and/or services contemplated in this RFP in the event of specified occurrence ; Bidder’s critical supplier strategy to ensure continuity of suppliers in such event; and Bidders  process or criteria for prioritizing customer demands during a crisis.

## Conformity of Proposal with SGC Requirements

Bidders represent and warrant that the goods and/or services provided in their Proposal will meet SGC’s requirements as expressed in the Scope of Work contained in this RFP and will be fit for the purpose expressed herein.

# Vendor Requirements

## Proposal

Successful Bidders should expect that their response to the RFP and any accompanying supporting materials will be incorporated into any contract signed with SGC.

## Standard Service Agreement

Successful Bidder will be expected to sign SGC’s standard services agreement, subject to such changes as are necessary to reflect the terms of this RFP and Successful Bidder’s bid or proposal, and such further changes as the parties, acting reasonably, may agree.

## Seneca Nation Business Registration Fee (SNIBRF)

Vendor must pay the SNIBRF of $750 directly to the Seneca Gaming Authority once total 		payment to the vendor exceeds $10,000.  Failure to pay the fee when required may 			result in termination of further business with Seneca Gaming Corporation.

# Bidder Certifications and Representations

Bidder is a reputable company fully qualified and regularly engaged in providing products and/or services necessary to meet the terms, conditions and requirements of the RFP.

Bidder is aware of, is fully informed about, and is in full compliance with all applicable federal, state and local laws, rules, regulations and ordinances.

Bidder understands the requirements and specifications set forth in this RFP and affirms that no compensation has been received for participation in the preparation of the specifications for this RFP.

Bidder has reviewed and understood SGC’s Standard Terms & Conditions found at https://senecacasinos.com/media/zqdd2j1f/sgc-standard-terms-and-conditions-v-10-30-20.pdf

Bidder represents and warrants that all goods and services quoted in response to this RFP will meet or exceed the safety standards established and promulgated under the Federal Occupational Safety and Health Law (Public Law 91-596) and its regulations in effect or proposed as of the date of this solicitation.

All statements, information and representations prepared and submitted in response to this RFP are current, complete, true and accurate. Bidder acknowledges that SGC will rely on such statements, information and representations in selecting the Awarded Vendor. If selected by SGC as the Awarded Vendor, Bidder will notify SGC immediately of any material change in any matters with regard to which Bidder has made a statement or representation or provided information.

I, the undersigned, hereby certify that I am authorized to sign as a representative for the Bidder listed below:

Legal Name of Bidder: ___________________________________________________

DBA (if applicable): _____________________________________________________

Address: ______________________________________________________________

Telephone: ____________________

E-Mail: _______________________________________________________________

Website: ______________________________________________________________

Representative’s Signature: _______________________________________________

Representative’s Printed Name: ____________________________________________

Representative’s Printed Title: _____________________________________________

Date: __________________			NAICS code # 	______________________