## Instructions
BIDDER INSTRUCTIONS:
Please complete the following tabs as instructed (in each tab):
Tab 2 - Bidder Overview
Tab 3 - Scope of Work
Tab 4 - Bidder Questions
Tab 5 - Pricing

## Overview
ID | BIDDER OVERVIEW
1 | Bidder Name
2 | Location
3 | In Business Since
4 | # of Employees
5 | # of Clients
6 | Industries Served
7 | Company Overview
8 | Product Solution Overview
9 | Service Overview

## SOW
ID | SCOPE OF WORK
1 | SENECA NIAGARA RESORT & CASINO
2 | SNRC is seeking a qualified vendor to repair or replace the existing area of refuge system (current system specs below) at the Seneca Niagara Resort & Casino.
3 | Existing System: at 310 4th Street, Niagara Falls, NY 14303
4 | Type: Area of Refuge / Emergency Communication System
5 | Manufacturer: Housing Device, Inc.
6 | COMPONENTS
7 | Master Station: Model HDI-ADA-100 MS-30; QTY: 2
8 | Call Stations: HDI-ADA-100A; QTY: 56
9 | NORTH STAIRWELL LOCATIONS (ECHO 2)
10
11 | SOUTH STAIRWELL LOCATIONS (ECHO 2)
12
13 | Provisions:
14 | 1.) Repair or replace the existing Area of Refuge system to the following minimum specifications:
15 | Must be ADA Compliant, signage must clearly states that this is an area of refuge with an accessibility logo and must be no higher than 48" from the ground.
16 | Area of Refuge Identification- - Each Area of Refuge entrance shall be identified with a sign reading “ Area of Refuge” - Where it applies, which is each door providing access to an Exterior Areas of Assisted Rescue should be identified with a sign reading “ Exterior Area of Assisted Rescue” - The identification signs should include the International Symbol of Accessibility. (wheelchair)
17 | Accessibility Requirements- - Raised tactile uppercase characters - Grade 2 Braille located directly below the tactile text - High contrast lettering on a non-glare background - Installation adjacent to the latch side of the door whenever practical, with the baseline of the tactile characters mounted between 48 inches and 60 inches above the floor.
18 | Illumination- - Where exit signs are required to be illuminated, the Area of Refuge identification signs should also be illuminated.
19 | Directional Signage- - Directional signage should be provided wherever accessible means of egress or Area of Refuge is not immediately obvious. (Inaccessible exits, elevator lobbies, corridor intersections, within large floor plans) The intent is to help direct occupants at every decision point who require accessible means of egress to the nearest compliant route. These should include the International Symbol of Accessibility.
20 | Emergency Instruction Signage- - A statement at the Area of Refuge advising occupants who are able to use the stairs to do so. (ex. Persons who are able to use the stairs should proceed to the nearest exit stairway and continue to exit the building). - Any information describing how occupants requiring assistance will receive assistance during an emergency. (ex. Persons unable to use the stairs should remain in this Area of Refuge and await assistance from emergency responders or designated building personnel). - Operating instructions for the two-way communication system where they are provided. (ex. To contact emergency personnel, press the emergency call button and wait for a response. Remain in this Area of Refuge unless instructed otherwise or conditions become unsafe). It might be good to put something like a floor level or a stairway identification on the instructional signage. That is not specifically required by code however. Or, the number for Security Dispatch, that is good practice too but again, not required.
21 | All necessary equipment to the following minimum requirements:
22 | Master Stations QTY 1 or 2: Cornell A-4212 or approved equivalent (location of install subject to change)
23 | Call Stations QTY 56: Cornell Sentinel 4200 Series Analog or approved equivalent
24 | Any modifications required to accommodate the replacement system proposed shall be completed by the awarded vendor within this scope of work and included in the cost of materials and labor.
25 | Proposal for upgrade must include:
26 | (a) All necessary equipment and hardware for repair or replacement of existing system
27 | (b) Proposed solutions must demonstrate full compatibility with the existing infrastructure and electrical systems
28 | (c)Proposals should include all required hardware, software, and labor for upgrade including 4 hours of training on new system.
29 | 2.)Repalcement of all applicable AoR lighting and signage to comply with current standard and codes. Additional signage needed as applicable.
30 | Labor for installation must include the following:
31 | (a)Removal and disposal of all materials and equipment from existing and outgoing system (LED Panels, ancillary equipment, packaging).
32 | (b)Integration (including electrical) at existing equipment locations and potential new locations for master stations. All equipment must be compliant with any applicable codes and compliance upon completion.
33 | (c)Any travel expenses for installation team
34 | (d)System wiring to comply with EIA and NEC standards and all applicable state and local codes
35 | Submittals:
36 | 1.) Literature shall be provided that indicate dimensions, weights, capabilities of all aspects of hardware and software included in proposal
37 | 2.) Any applicable warranties
38 | 3.) As ALTERNATE include extended warranties
39 | 4.) Preventative maintenance plan - based on manufacturer recommendation.
40 | 5.) Include pricing for up to 3 additional units including installation.
41 | SENECA ALLEGANY RESORT & CASINO
42 | As an option; SARC is seeking a qualified vendor to add one (1) master staton to (current system specs below) at the Seneca Allegany Resort & Casino. Must be compatible with system master station described below.
43 | Existing System: at 777 Seneca Allegany Boulevard
44 | Type: Area of Refuge / Emergency Communication System
45 | Manufacturer: Cornell Communications
46 | COMPONENTS
47 | Master Station: Cornell A-4212; QTY: 1
48 | Call Stations: Cornell Sentinel 4200 Series Analog; QTY: 11 are existing and do not require repalcement. Master station must be compatible with these call stations.
49 | SOUTHWEST STAIRWELL - NEW TOWER
50 | #VALUE!
51 | Provisions:
52 | 1.) Install one (1) master station in addition to existing Area of Refuge system at the dispatcher desk located in the back of building to the following minimum specifications:
53 | Must be ADA Compliant, signage must clearly states that this is an area of refuge with an accessibility logo and must be no higher than 48" from the ground.
54 | Area of Refuge Identification- - Each Area of Refuge entrance shall be identified with a sign reading “ Area of Refuge” - Where it applies, which is each door providing access to an Exterior Areas of Assisted Rescue should be identified with a sign reading “ Exterior Area of Assisted Rescue” - The identification signs should include the International Symbol of Accessibility. (wheelchair)
55 | Accessibility Requirements- - Raised tactile uppercase characters - Grade 2 Braille located directly below the tactile text - High contrast lettering on a non-glare background - Installation adjacent to the latch side of the door whenever practical, with the baseline of the tactile characters mounted between 48 inches and 60 inches above the floor.
56 | Illumination- - Where exit signs are required to be illuminated, the Area of Refuge identification signs should also be illuminated.
57 | Directional Signage- - Directional signage should be provided wherever accessible means of egress or Area of Refuge is not immediately obvious. (Inaccessible exits, elevator lobbies, corridor intersections, within large floor plans) The intent is to help direct occupants at every decision point who require accessible means of egress to the nearest compliant route. These should include the International Symbol of Accessibility.
58 | Emergency Instruction Signage- - A statement at the Area of Refuge advising occupants who are able to use the stairs to do so. (ex. Persons who are able to use the stairs should proceed to the nearest exit stairway and continue to exit the building). - Any information describing how occupants requiring assistance will receive assistance during an emergency. (ex. Persons unable to use the stairs should remain in this Area of Refuge and await assistance from emergency responders or designated building personnel). - Operating instructions for the two-way communication system where they are provided. (ex. To contact emergency personnel, press the emergency call button and wait for a response. Remain in this Area of Refuge unless instructed otherwise or conditions become unsafe). It might be good to put something like a floor level or a stairway identification on the instructional signage. That is not specifically required by code however. Or, the number for Security Dispatch, that is good practice too but again, not required.
59 | All necessary equipment to the following minimum requirements:
60 | Master Stations QTY 1: Cornell A-4212 or approved equivalent (location of install subject to change)
61 | Any modifications required to accommodate the replacement system proposed shall be completed by the awarded vendor within this scope of work and included in the cost of materials and labor.
62 | Proposal for upgrade must include:
63 | (a) All necessary equipment and hardware for repair or replacement of existing system
64 | (b) Proposed solutions must demonstrate full compatibility with the existing infrastructure and electrical systems
65 | (c)Proposals should include all required hardware, software, and labor for upgrade including 4 hours of training on new system.
66 | 2.)Repalcement of all applicable AoR lighting and signage to comply with current standard and codes. Additional signage needed as applicable.
67 | Labor for installation must include the following:
68 | (a)Integration at new locations for master station.
69 | (b)Integration (including electrical) at existing equipment locations and potential new locations for master stations. All equipment must be compliant with any applicable codes and compliance upon completion.
70 | (c)Any travel expenses for installation team
71 | (d)System wiring to comply with EIA and NEC standards and all applicable state and local codes
72 | Submittals:
73 | 1.) Literature shall be provided that indicate dimensions, weights, capabilities of all aspects of hardwareand software included in proposal
74 | 2.) Any applicable warranties
75 | 3.) As ALTERNATE include extended warranties
76 | 4.) Preventative maintenance plan - based on manufacturer recommendation.
77 | 5.) Include pricing for up to 3 additional units including installation.
78 | END OF SOW

## Bidder Questions
INSTRUCTIONS: Please answer YES or NO to all questions below by placing an "X" in the appropriate column. Add any additional information in the COMMENTS column as needed or required. Please provide as much detail as possible.
ID | VENDOR MINIMUM REQUIREMENTS | YES | NO | COMMENTS
1 | Are you able to meet the specifications provided? If No, please explain in Comments section.
2 | Can you confirm your typical work days & times?
3 | Can you confirm the lead time required for you to have all materials available & on site to complete the SOW?
4 | Can you confirm your earliest availability to start?
5 | Do you provide any discounts, such as early payment? If Yes, please explain in the Comments section.
6 | Will you accept SGC's Terms & Conditions as mentioned in the RFP document? If No, please explain in Comments section.
7 | Do you understand the TERO Requirements involved?
8 | Can you provide any warranties associated with the equipment and/or installation?
9 | Are there any tariffs associated with your quotation?
10 | Can you confirm the number of technicians that will be installing the system and how many days it will take to complete?

## Pricing
INSTRUCTIONS: Please provide a clear review of all pricing and pricing terms for the Scope of Services specified in Exhibit A tab 3.
SNRC PRICING & PRICING TERMS | QTY | PRICE | TOTAL
Cornell A-4212 or approved equivalent (MATERIALS) | 2 | 0 | 0
Cornell Sentinel 4200 Series Analog or approved equivalent (MATERIALS) | 56 | 0 | 0
Installation (LABOR) | 1 | 0 | 0
SUBTOTAL | - | - | 0
TERO (5%) - Tribal Employment Rights Ordinance | - | 5% | 0
TOTAL | - |  | 0
Extended Warranty Option | - |  | 0
Preventative Maintenance Plan Option | - |  | 0
Option: Pricing per unit for up to QTY 3x Additional Call-Station (Sentinel 4200 Analog or approved equivalent) Units | - |  | 0
SARC PRICING & PRICING TERMS | QTY | PRICE | TOTAL
Cornell A-4212 or approved equivalent (MATERIALS) | 1 | 0 | 0
Installation (LABOR) | 1 | 0 | 0
SUBTOTAL | - | - | 0
TOTAL | - |  | 0
Extended Warranty Option | - |  | 0
Preventative Maintenance Plan Option | - |  | 0
Option: Pricing per unit for up to QTY 3x Additional Call-Station (Sentinel 4200 Analog or approved equivalent) Units | - |  | 0