## Instructions
BIDDER INSTRUCTIONS:
Please complete the following tabs as instructed (in each tab):
Tab 2 - Bidder Overview
Tab 3 - Scope of Work
Tab 4 - Bidder Questions
Tab 5 - Pricing

## Overview
ID | BIDDER OVERVIEW
1 | Bidder Name
2 | Location
3 | In Business Since
4 | # of Employees
5 | # of Clients
6 | Industries Served
7 | Company Overview
8 | Product Solution Overview
9 | Service Overview

## SOW
ID | SPECIFICATIONS & SCOPE OF WORK
Due to failure of a Grindex Submersible Pump SARC is seeking a qualified vendor to replace (remove & dispose old unit, supply & install new unit) existing 90 HP Grindex Submersible Pump.
The intent is to purchase the following Grindex Submersible Pump or equivalent.
Qty (1) 90 HP GRINDEX Submerisible Pump:
A. Model Type 8108.010-0056
B. Voltage-460-3-60
C. Built-In VFD NEMA 3R
Provisions:
1. Supply 90 HP Grindex Submersible Pump or equivalent.
2. Drain settling pump-sump and any other components of the system to remain to confirm all components are installed in accordance with manufacturer’s recommendations. Refer to Grindex Installation, Operation & Maintenance Manual attached.
3. Jet and scope existing piping to confirm no partial obstructions exist within the system piping.
4. Furnish and install new 90 HP Grindex Submersible Pump 3 Phase, 60 Cycle 460V, 1190 RPM, Type L8108-010-0056 - Refer to data tag photo in attached document: Pond Pump.jpg. Provide all necessary gaskets, valves, oil, and other accessories necessary for a complete installation of the new pump in accordance with manufacturer’s recommendations..
5. Provide air test to confirm no leaks are present in the system prior to startup.
6. Provide start up and testing to verify connections and monitor performance (flow rate, pressure, etc.) after the pump is submerged and turned on.
7. Coordinate start up with SGC’s Electrician to be present to record data to determine if there is any voltage drop or other power supply concerns associated with the pump.
8. Provide standard warranty documentation for pump.
Submittals:
1. Literature shall be provided that indicate dimensions, operating and shipping weights, capacities, ratings, factory supplied accessories, connection requirements. Operation, service, and maintenance manual with start-up requirements.
2. Bidder responses should include any references from customers where such work has been performed previously.
3. Bidders are invited to submit bid responses on all or part of the items listed in the scope of work.
Constraints
1. Electrical Power to be connected to existing service at the unit.
2. Work may be completed on dayshift, Monday thru Friday. 7am to 5pm
3. It will take 6 or 7 hours to fill pond once the unit is installed.
END OF SOW

## Bidder Questions
INSTRUCTIONS: Please answer YES or NO to all questions below by placing an "X" in the appropriate column. Add any additional information in the COMMENTS column as needed or required. Please provide as much detail as possible.
ID | VENDOR MINIMUM REQUIREMENTS | YES | NO | COMMENTS
1 | Are you able to meet the specifications provided? If No, please explain in Comments section.
2 | Can you confirm your typical work days & times?
3 | Can you confirm the lead time required for you to have all materials available & on site to complete the SOW?
4 | Can you confirm your earliest availability to start?
5 | Do you provide any discounts, such as early payment? If Yes, please explain in the Comments section.
6 | Do you understand the TERO Requirements as specified in the RFP document?
7 | Will you accept SGC's Terms & Conditions as mentioned in the RFP document? If No, please explain in Comments section.
8 | Can you include any exclusions you may have as part of your proposal?

## Pricing
INSTRUCTIONS: Please provide a clear review of all pricing and pricing terms for the Scope of Services specified in Exhibit A tab 3.
PRICING & PRICING TERMS